Opti-Pac Durable PH

- General

  - Air filters shall be medium or high efficiency ASHRAE box style filters consisting of dual layered synthetic media, thermoplastic resin separators, and a double walled extruded polystyrene enclosing frame

  - Sizes shall be noted on drawings or other supporting materials

- Construction

  - Filter media shall be of one continuous sheet of synthetic mat filter media formed into uniformly spaced pleats and formed into a mini-pleat pack configuration

  - Thermoplastic pleat separators shall provide uniform media separation to promote uniform airflow throughout the media.

  - The enclosing frame shall be of plastic construction and bonded to the entire periphery of the media pack to prevent air bypass

  - Filter frame shall be double walled design for increased filter strength

- Performance

  - The filter shall have a Minimum Efficiency Reporting Value of MERV (11, 13, 15) when evaluated under ASHRAE Standard 52.2 and MERV 11A,11A and 13A when evaluated under 52.2 with Appendix J.

  - Initial resistance to airflow shall be 0.55”, 0.52”, 0.68”w.g for a 4” deep model at an airflow of  500 fpm.

  - The filter shall be listed by Underwriters Laboratories as UL Class 900

  - The filters shall be capable of withstanding 10.0”w.g. without failure of the media pack.

  - Recommended filter change out resistance is 1.5” w.g.

  - Manufacturer shall provide evidence of facility certification to ISO 9001:2015.